MXC-HIF1

외부통신 프로토콜

2026년 03월 07일

전략부품개발팀

| 결 재 | 기안 | 검토 | 검토 | 승인 |
| --- | --- | --- | --- | --- |
|  | / | / | / | / |

목차

1.	통신 개요	3

1.	통신 방식	4

2.	통신 속도	4

3.	통신 주기	4

4.	구성도	4

5.	통신 예시	5

2.	UART 설정	6

1.	통신 입출력 단자(추후 2선식으로 변경 예정)	7

2.	통신 설정	7

3.	Function Code	7

1.	READ	8

2.	Write	8

4.	장치별 맵	8

1.	Backup Interface	9

2.	Digital Input-Output	9

3.	Heating Jacket	9

4.	H2 Detector	11

5.	H2 Detector(TFT)	11

5.	Scale 정의	14

1.	온도	15

2.	압력	15

3.	농도	15

- 통신 개요

  - 통신 방식

    - RS 485

    - 5Wire(TXD+, TXD-, RXD+, RXD-, GND)

    - Modbus RTU

  - 통신 속도

    - Uart4 : 19,200bps(Modbus RTU).

    - Lpuart1 : 38,400bps(Modbus RTU).

    - Usart1 : 19,200bps(User Protocal).

    - Usart2 : 19,200bps(Modbus RTU).

    - Usart3 : 9,600bps(Modbus RTU).

  - 통신 주기

    - PLC → Interface Board : 최소 100ms.

  - 구성도

  - 통신 예시

예)

DIO_SUB1의 ID(국번) 1로 가정 할 때 Write Multiple Registers를

이용하여 주소 129번에 PLC가 DIO_SUB1에 0xFFFF 쓰기 요청한다.

쓰기 요청 프레임(HEX) : 01 10 00 81 00 01 02 FF FF B9 F1

예)

DIO_SUB1의 ID(국번) 1로 가정 할 때 Read Hoding Registers를

이용하여 주소 130번에 PLC가 DIO_SUB1에 읽기 요청한다.

읽기 요청 프레임(HEX) : 01 03 00 82 00 01 24 22

예)

Gas Detector의 ID(국번)를 1로 가정할 때
 Read Holding Registers를 이용하여
 주소 30001(측정 가스 농도)에 대해 PLC가 Gas Detector로부터 데이터를 읽는다.

읽기 요청 프레임 (HEX) : 01 03 75 30 00 01 9E 09

예)

Gas Detector의 ID(국번)를 1로 가정할 때
 Write Multiple Registers를 이용하여
 주소 5번(CH1 Measured Gas Concentration Upper Word) 에
 PLC가 0x0001을 쓰기 요청한다.

쓰기 요청 프레임 (HEX) : 01 10 00 05 00 01 02 00 01 67 C5

- UART 설정

  - 통신 입출력 단자(추후 2선식으로 변경 예정)

| 핀 번호 | 역할 | 비고 |
| --- | --- | --- |
| 1 | TX+ | 사용 |
| 2 | TX- | 사용 |
| 3 | RX- |  |
| 4 | RX+ |  |
| 5 | GND |  |

  - 통신 설정

Uart4, Lpuart1, Usart2, Usart1

| Parameter | Value | Parameter | Value |
| --- | --- | --- | --- |
| Data Bits | 8bits | Parity Bits | None |
| Stop Bits | 1bit | Flow Control | None |
| Bit Order | LSB first |  |  |

Usart3

| Parameter | Value | Parameter | Value |
| --- | --- | --- | --- |
| Data Bits | 8bits | Parity Bits | Even |
| Stop Bits | 1bit | Flow Control | None |
| Bit Order | LSB first |  |  |

- Function Code

  - READ

- 프로토콜 표 참조

  - Write

- 프로토콜 표 참조

※ 상기 Function code 만 사용 가능함.

※ 상기 외 명령은 무응답.

- 장치별 맵

  - Backup Interface

| Address | FC Type | R/W | Item | Data type | Note |
| --- | --- | --- | --- | --- | --- |
| Backup Interface |  |  |  |  |  |
| 199 | Read Holding Register | R | Heart Beat | Uint16 | 0bit : DIO_Sub 1bit : Heating Jecket 2bit : Gas detector 3bit : Backup Interface 1일때 정상 0일때 비정상 |
| 200 | Read Holding Register | R | Heart Beat(PLC – Interface Module) | Uint16 | • 0~65536 범위 내 통신 주기 마다 증가 • Reset 시 시퀀스 번호를 0으로 초기화 |
| 201~241 | Write MultipleRegister | W | User Data | Uint16 |  |
| 242~282 | Read Holding Register | R | User Data | Uint16 |  |
| 283~322 | Reserved |  |  |  |  |

  - Digital Input-Output

| Address | FC Type | R/W | Item | Data type | Note |
| --- | --- | --- | --- | --- | --- |
| Digital Input-Output |  |  |  |  |  |
| 129 | Write MultipleRegister | W | DO Write Command | Uint16 | 국번 1, 2번으로 선택 |
| 130 | Read Holding Register | R | DI Read Command | Uint16 | 국번 1, 2번으로 선택 |

  - Heating Jacket

| Address | FC Type | R/W | Item | Data type | Note |
| --- | --- | --- | --- | --- | --- |
| Heating jacket |  |  |  |  |  |
| 1000 | Read Input Register (Read Only) | R | CH1 히터 온도 | int16 |  |
| 1001 |  | R | CH2 히터 온도 | int16 |  |
| 1002 |  | R | CH3 히터 온도 | int16 |  |
| 1003 |  | R | CH4 히터 온도 | int16 |  |
| 1004 |  | R | CH5 히터 온도 | int16 |  |
| 1005 |  | R | CH6 히터 온도 | int16 |  |
| 1006 |  | R | CH7 히터 온도 | int16 |  |
| 1007 |  | R | CH8 히터 온도 | int16 |  |
| 1008 |  | R | CH9 히터 온도 | int16 |  |
| 1009 |  | R | CH10 히터 온도 | int16 |  |
| 1010 |  | R | CH11 히터 온도 | int16 |  |
| 1011 |  | R | CH12 히터 온도 | int16 |  |
| 1012 |  | R | CH13 히터 온도 | int16 |  |
| 1013 |  | R | CH14 히터 온도 | int16 |  |
| 1014 |  | R | CH15 히터 온도 | int16 |  |
| 1015 |  | R | CH16 히터 온도 | int16 |  |
| 1016 |  | R | CH17 히터 온도 | int16 |  |
| 1017 |  | R | CH18 히터 온도 | int16 |  |
| 1018 |  | R | 1CH 알람 | int16 |  |
| 1019 |  | R | 2CH 알람 | int16 |  |
| 1020 |  | R | 3CH 알람 | int16 |  |
| 1021 |  | R | 4CH 알람 | int16 |  |
| 1022 |  | R | 5CH 알람 | int16 |  |
| 1023 |  | R | 6CH 알람 | int16 |  |
| 1024 |  | R | 7CH 알람 | int16 |  |
| 1025 |  | R | 8CH 알람 | int16 |  |
| 1026 |  | R | 9CH 알람 | int16 |  |
| 1027 |  | R | 10CH 알람 | int16 |  |
| 1028 |  | R | 11CH 알람 | int16 |  |
| 1029 |  | R | 12CH 알람 | int16 |  |
| 1030 |  | R | 13CH 알람 | int16 |  |
| 1031 |  | R | 14CH 알람 | int16 |  |
| 1032 |  | R | 15CH 알람 | int16 |  |
| 1033 |  | R | 16CH 알람 | int16 |  |
| 1034 |  | R | 17CH 알람 | int16 |  |
| 1035 |  | R | 18CH 알람 | int16 |  |
| 2000 | Holding Register (Read/ Write) | R/W | Machine ON/OFF | int16 |  |
| 2001 |  | R /W | EEPROM Save | int16 |  |
| 2002 |  | R /W | ALARM Reset | int16 |  |
| 2003 |  | R /W | 1CH SV 온도 설정 | Uint16 |  |
| 2004 |  | R /W | 2CH SV 온도 설정 | Uint16 |  |
| 2005 |  | R /W | 3CH SV 온도 설정 | Uint16 |  |
| 2006 |  | R /W | 4CH SV 온도 설정 | Uint16 |  |
| 2007 |  | R /W | 5CH SV 온도 설정 | Uint16 |  |
| 2008 |  | R /W | 6CH SV 온도 설정 | Uint16 |  |
| 2009 |  | R /W | 7CH SV 온도 설정 | Uint16 |  |
| 2010 |  | R /W | 8CH SV 온도 설정 | Uint16 |  |
| 2011 |  | R /W | 9CH SV 온도 설정 | Uint16 |  |
| 2012 |  | R /W | 10CH SV 온도 설정 | Uint16 |  |
| 2013 |  | R /W | 11CH SV 온도 설정 | Uint16 |  |
| 2014 |  | R /W | 12CH SV 온도 설정 | Uint16 |  |
| 2015 |  | R /W | 13CH SV 온도 설정 | Uint16 |  |
| 2016 |  | R /W | 14CH SV 온도 설정 | Uint16 |  |
| 2017 |  | R /W | 15CH SV 온도 설정 | Uint16 |  |
| 2018 |  | R /W | 16CH SV 온도 설정 | Uint16 |  |
| 2019 |  | R /W | 17CH SV 온도 설정 | Uint16 |  |
| 2020 |  | R /W | 18CH SV 온도 설정 | Uint16 |  |

  - Gas Detector

| Address | FC Type | R/W | Item | Data type | Note |
| --- | --- | --- | --- | --- | --- |
| H2 Detector |  |  |  |  |  |
| 30000 | Read Input Resgisters | R | 측정가스 농도 | Uint16 |  |
| 30001 |  | R | High Scale 설정값 | Uint16 |  |
| 30002 |  | R | 1차 Alarm 설정값 | Uint16 |  |
| 30003 |  | R | 2차 Alarm 설정값 | Uint16 |  |
| 10001 | Read Discrete Input | R | Alarm1 | Bit |  |
| 10002 |  | R | Alarm2 | Bit |  |
| 10003 |  | R | Fault Bit | Bit |  |
| 10004 |  | R | MENU Mode | Bit |  |
| 10005 |  | R | Test | Bit |  |
| 10006 |  | R | CAL | Bit |  |
| 10007 |  | R | Reserved | Bit |  |
| 10008 |  | R | Toggle Bit | Bit |  |
| 3 | Read&Write Coils | R/W | Gas Detector Test Pattern On(Write 0xff) | Uint16 |  |
| 2 |  | R/W | Gas Detector Normal Operation restart(Write 0x00) | Uint16 |  |

  - Gas Detector(TFT)

| Address | FC Type | R/W | Item | Data type | Note |
| --- | --- | --- | --- | --- | --- |
| H2 Detector(TFT) |  |  |  |  |  |
| 1 | Read & Write Coils | R | CH1 Remote Test Mode Reset | Bit |  |
| 2 |  | R | CH1 Remote Test Mode Set | Bit |  |
| 3 |  | R | CH2 Remote Test Mode Reset | Bit |  |
| 4 |  | R | CH2 Remote Test Mode Set | Bit |  |
| 1 | Read Discrete Input | R | CH1 Alarm-1 Active | Bit |  |
| 2 |  | R | CH1 Alarm-2 Active | Bit |  |
| 3 |  | R | CH1 Trouble(Fault) Active | Bit |  |
| 4 |  | R | CH1 Maintenance Mode | Bit |  |
| 5 |  | R | CH1 Test Mode | Bit |  |
| 6 |  | R | CH1 Calibration Mode | Bit |  |
| 8 |  | R | CH1 Toggle bit | Bit |  |
| 9 |  | R | CH2 Alarm-1 Active | Bit |  |
| 10 |  | R | CH2 Alarm-2 Active | Bit |  |
| 11 |  | R | CH2 Trouble(Fault) Active | Bit |  |
| 12 |  | R | CH2 Maintenance Mode | Bit |  |
| 13 |  | R | CH2 Test Mode | Bit |  |
| 14 |  | R | CH2 Calibration Mode | Bit |  |
| 16 |  | R | CH2 Toggle bit | Bit |  |
| 1 | Read Input Register | R/W | CH1 Detector Status-1 | Uint16 |  |
| 2 |  | R/W | CH1 Trouble (Fault) Code | Uint16 |  |
| 3 |  | R/W | CH1 Decimal Point & Unit | Uint16 |  |
| 4 |  | R/W | CH1 Measured Gas Concentration Lower Word | Uint16 |  |
| 5 |  | R/W | CH1 Measured Gas Concentration Upper Word | Uint16 |  |
| 6 |  | R/W | CH1 Measured Gas Concentration | Uint16 |  |
| 7 |  | R/W | CH1 Alarm-1 Set Point Lower Word | Uint16 |  |
| 8 |  | R/W | CH1 Alarm-1 Set Point Upper Word | Uint16 |  |
| 9 |  | R/W | CH1 Alarm-1 Set Point | Uint16 |  |
| 10 |  | R/W | CH1 Alarm-2 Set Point Lower Word | Uint16 |  |
| 11 |  | R/W | CH1 Alarm-2 Set Point Upper Word | Uint16 |  |
| 12 |  | R/W | CH1 Alarm-2 Set Point | Uint16 |  |
| 13 |  | R/W | CH1 High Scale Lower Word | Uint16 |  |
| 14 |  | R/W | CH1 High Scale Upper Word | Uint16 |  |
| 15 |  | R/W | CH1 High Scale | Uint16 |  |
| 21 |  | R/W | CH2 Detector Status-1 | Uint16 |  |
| 22 |  | R/W | CH2 Trouble(Fault) Code | Uint16 |  |
| 23 |  | R/W | CH2 Decimal Point & Unit | Uint16 |  |
| 24 |  | R/W | CH2 Measured Gas Concentration Lower Word | Uint16 |  |
| 25 |  | R/W | CH2 Measured Gas Concentration Upper Word | Uint16 |  |
| 26 |  | R/W | CH2 Measured Gas Concentration | Uint16 |  |
| 27 |  | R/W | CH2 Alarm-1 Set Point Lower Word | Uint16 |  |
| 28 |  | R/W | CH2 Alarm-1 Set Point Upper Word | Uint16 |  |
| 29 |  | R/W | CH2 Alarm-1 Set Point | Uint16 |  |
| 30 |  | R/W | CH2 Alarm-2 Set Point Lower Word | Uint16 |  |
| 31 |  | R/W | CH2 Alarm-2 Set Point Upper Word | Uint16 |  |
| 32 |  | R/W | CH2 Alarm-2 Set Point | Uint16 |  |
| 33 |  | R/W | CH2 High Scale Lower Word | Uint16 |  |
| 34 |  | R/W | CH2 High Scale Upper Word | Uint16 |  |
| 35 |  | R/W | CH2 High Scale | Uint16 |  |
| 85 |  | R/W | CH1 Detector Status2 | Uint16 |  |
| 86 |  | R/W | CH2 Detector Status2 | Uint16 |  |
| 89 |  | R/W | Heart beat | Uint16 |  |
| 91 |  | R/W | Detector Serial Number-1 | Uint16 |  |
| 92 |  | R/W | Detector Serial Number-2 | Uint16 |  |
| 93 |  | R/W | Detector Serial Number-3 | Uint16 |  |
| 94 |  | R/W | Detector Serial Number-4 | Uint16 |  |
| 95 |  | R/W | Detector Serial Number-5 | Uint16 |  |
| 96 |  | R/W | Detector Serial Number-6 | Uint16 |  |
| 1 | Read & Write Holding Registers | R/W | CH1 Detector Status-1 | Uint16 |  |
| 2 |  | R/W | CH1 Trouble(Fault) Code | Uint16 |  |
| 3 |  | R/W | CH1 Decimal Point & Unit | Uint16 |  |
| 4 |  | R/W | CH1 Measured Gas Concentration Lower Word | Uint16 |  |
| 5 |  | R/W | CH1 Measured Gas Concentration Upper Word | Uint16 |  |
| 6 |  | R/W | CH1 Measured Gas Concentration | Uint16 |  |
| 7 |  | R/W | CH1 Alarm-1 Set Point Lower Word | Uint16 |  |
| 8 |  | R/W | CH1 Alarm-1 Set Point Upper Word | Uint16 |  |
| 9 |  | R/W | CH1 Alarm-1 Set Point | Uint16 |  |
| 10 |  | R/W | CH1 Alarm-2 Set Point Lower Word ( | Uint16 |  |
| 11 |  | R/W | CH1 Alarm-2 Set Point Upper Word | Uint16 |  |
| 12 |  | R/W | CH1 Alarm-2 Set Point | Uint16 |  |
| 13 |  | R/W | CH1 High Scale Lower Word | Uint16 |  |
| 14 |  | R/W | CH1 High Scale Upper Word | Uint16 |  |
| 15 |  | R/W | CH1 High Scale | Uint16 |  |
| 21 |  | R/W | CH2 Detector Status-1 | Uint16 |  |
| 22 |  | R/W | CH2 Trouble(Fault) Code | Uint16 |  |
| 23 |  | R/W | CH2 Decimal Point & Unit | Uint16 |  |
| 24 |  | R/W | CH2 Measured Gas Concentration Lower Word | Uint16 |  |
| 25 |  | R/W | CH2 Measured Gas Concentration Upper Word | Uint16 |  |
| 26 |  | R/W | CH2 Measured Gas Concentration | Uint16 |  |
| 27 |  | R/W | CH2 Alarm-1 Set Point Lower Word | Uint16 |  |
| 28 |  | R/W | CH2 Alarm-1 Set Point Upper Word | Uint16 |  |
| 29 |  | R/W | CH2 Alarm-1 Set Point | Uint16 |  |
| 30 |  | R/W | CH2 Alarm-2 Set Point Lower Word | Uint16 |  |
| 31 |  | R/W | CH2 Alarm-2 Set Point Upper Word | Uint16 |  |
| 32 |  | R/W | CH2 Alarm-2 Set Point | Uint16 |  |
| 33 |  | R/W | CH2 High Scale Lower Word | Uint16 |  |
| 34 |  | R/W | CH2 High Scale Upper Word | Uint16 |  |
| 35 |  | R/W | CH2 High Scale | Uint16 |  |
| 85 |  | R/W | CH1 Detector Status-2 | Uint16 |  |
| 86 |  | R/W | CH2 Detector Status-2 | Uint16 |  |
| 89 |  | R/W | Heart beat | Uint16 |  |
| 91 |  | R/W | Detector Serial Number-1 | Uint16 |  |
| 92 |  | R/W | Detector Serial Number-2 | Uint16 |  |
| 93 |  | R/W | Detector Serial Number-3 | Uint16 |  |
| 94 |  | R/W | Detector Serial Number-4 | Uint16 |  |
| 95 |  | R/W | Detector Serial Number-5 | Uint16 |  |
| 96 |  | R/W | Detector Serial Number-6 | Uint16 |  |

- Scale 정의

  - 온도

45.3℃ → 453

  - 압력

1.25bar → 125

  - 농도

1.234ppm → 1234

※ 데이터 형은 Int16

※ 온도 x10, 압력 x100, 농도 x100